## AG01
Title | [8 empty] | Doc.no. |  |  | Operator |  | Sec.no.
Piping and Valve Specification | [8 empty] | 5060 |  |  |  |  | 3
[9 empty] | Project |  |  |  |  | Rev.no. | Rev.date |  | Page: Of:
Piping Class Sheet: |  |  | AG01 |  | d) h) |  | CL150 | [6 empty] | 05 | 01.10.2010 |  | 1 | 2
DESIGN CODE: |  |  | ASME B31.3 | [5 empty] | Corr. Allow: |  |  | 1.5 | mm | Material Selection : TCD 4650
Maximum Design Pressure: |  |  |  |  | Barg |  | 19.6 | 19.6 | 19.2
At Temperature: |  |  |  |  | °C |  | -15 | 38 | 50 | f)
PIPE SIZE AND WALL THICKNESS
Nom.Size(in) | 0.5 | 0.75 | 1 | 1.5 | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14
Dia.(mm) | 21.3 | 26.7 | 33.4 | 48.3 | 60.3 | 88.9 | 114.3 | 168.3 | 219.1 | 273.1 | 323.9 | 355.6
Wall th.(mm) | 3.73 | 3.91 | 4.55 | 5.08 | 5.54 | 5.49 | 6.02 | 7.11 | 6.35 | 6.35 | 6.35 | 7.92
Schedule |  |  | 80 |  |  |  | 40 |  |  | 20
WALL THICKNESS UNDER TOLERANCES: | [8 empty] | -12.5 | %
LONGITUDINAL WELD EFFICIENCY: | [8 empty] | 1.0
ELEMENT |  | DIMENSION STANDARDS | [6 empty] | NOM. SIZE |  | TYPE |  |  | MATERIAL |  | MDS | EDS
NAME | [8 empty] | FROM TO |  |  |  |  | NAME
[9 empty] | incl | incl
PIPE |  | ASME B36.10M | [6 empty] | 0.5 | 2 | Seamless, TE,NPT |  |  | A106 Gr.B Galv. |  | G01 | NGZ1
[14 empty] | to ASTM A123 |  |  | d)
|  | ASME B36.10M | [5 empty] | b) | 3 | 14 | Seamless, BE |  |  | A106 Gr.B |  | C01 | NGZ1
BENDING |  | Made from pipe | [14 empty] | NBE1
FITTINGS |  | ASME B16.11 | [6 empty] | 0.5 | 2 | CL3000 THR |  |  | A105 Galv. |  | G01 | EFI1/
[14 empty] | to ASTM A123 |  |  | EPI1
|  | ASME B16.9 | [5 empty] | b) | 3 | 14 |  |  |  | A234 WPB |  | C01 | EFI1
BRANCHES |  | Olets | [11 empty] | A105 |  | C01 | EBR5/
NOL1
|  | ASME B16.9 | [5 empty] | b) | As fittings |  |  |  |  | A234 WPB |  | C01 | EBR5
PIPE NIPPLE |  | ASTM A733 | [6 empty] | 0.5 | 2 | Sch XXS TBE |  |  | A106 Gr.B Galv. |  | G01 | EPI1
to ASTM A123
[9 empty] | 2 | 4 | TOE/BOE |  |  | A106 Gr.B |  | C01
SWAGE NIPP. |  | BS 3799 | [5 empty] | g) | 0.5 | 2 | min. Sch 160 |  |  | A106 Gr.B Galv. |  | G01 | EPI1
to ASTM A123
[9 empty] | 2 | 4 | TOE/BOE |  |  | A106 Gr.B |  | C01
FLANGES |  | ASME B16.5 | [6 empty] | 0.5 | 2 | CL150 RF THR. NPT |  |  | A105 Galv. |  | G01 | NAF1/
[14 empty] | to ASTM A123 |  |  | EPI1
[8 empty] | b) | 3 | 14 | CL150 RF WN |  |  | A105 |  | C01 | NAF1
FLG. BLIND |  | ASME B16.5 | [6 empty] | 0.5 | 14 | CL150 RF |  |  | A105 Galv. |  | G01 | NAF1
to ASTM A123
RED. THR'D |  | ASME B16.5 | [5 empty] | c) | 0.75 | 2 | CL150 RF NPT (F) |  |  | A105 Galv. |  | G01 | NAF1/
FLANGE | [16 empty] | EPI1
LINE BLINDS |  | Spect bl. | [6 empty] | 0.5 | 12 | CL150 FF |  |  | A516 Gr.70 Galv. |  | G01 | NLB1
to ASTM A123
|  | Spade/spacer | [6 empty] | 14 | 14 | CL150 FF |  |  | A516 Gr. 70 Galv. |  | G01 | NLB1
to ASTM A123
BOLTING |  | ASME B16.5 | [8 empty] | Stud bolts |  |  | A320 L7 Galv. |  | C100 | NBO1
[11 empty] | Hex. nuts |  |  | A194 7 Galv. |  | C100 | NBO1
GASKET |  | ASME B16.21 | [6 empty] | 0.5 | 14 | Thickness 1,5 mm | [5 empty] | NGA2
Gl.fibre w/NBR.binder
PLUGS |  | ASME B16.11 | [6 empty] | 0.5 | 1 | Hex. head scd. NPT |  |  | A105 Galv. |  | G01 | EPI1
to ASTM A123
SAFETY | [7 empty] | c) | 0.5 | 0.75 | NPT (M) |  |  | B446 N06625 |  |  | EFI4/
BLEED PLUG | [13 empty] | Annealed |  |  | EPI1
NOTES: | See page 2
Title | [8 empty] | Doc.no. |  |  | Operator |  | Sec.no.
Piping and Valve Specification | [8 empty] | 5060 |  |  |  |  | 3
[9 empty] | Project |  |  |  |  | Rev.no. | Rev.date |  | Page: Of:
Piping Class Sheet: |  |  | AG01 |  | d) h) |  | CL150 | [6 empty] | 05 | 01.10.2010 |  | 2 | 2
VALVE OR |  | VSM |  |  | NOMINAL SIZE |  |  |  | VDS |  |  | REMARKS
EQUIPMENT |  |  |  |  | FROM |  | TO
TYPE |  |  |  |  | incl |  | incl
GATE |  |  |  |  | 0.5 |  | 2 |  | GTRD01T |  |  | TE |  |  |  | f)
BUTTERFLY |  |  |  |  | 3 |  | 14 |  | BUAD21R |  |  | Wafer, RF |  |  |  | f)
[5 empty] | 3 |  | 14 |  | BUAD31R |  |  | Wafer, Metal seated, RF |  |  |  | f)
GLOBE |  |  |  |  | 0.5 |  | 1.5 |  | GBDD01T |  |  | TE |  |  |  | f)
CHECK |  |  |  |  | 0.5 |  | 2 |  | CHDD01T |  |  | TE |  |  |  | f)
BALL |  |  |  |  | 0.5 |  | 2 |  | BLAD01T |  |  | FB, TE |  |  |  | f)
[5 empty] | 0.5 |  | 8 |  | BLAD11R |  |  | FB, RF |  |  |  | f)
MODULAR |  |  |  |  | 0.5 |  | 2 |  | CBAD21D |  |  | SB, DB&B, RF/TE |  |  |  | f)
[5 empty] | 0.5 |  | 4 |  | CBAD01R |  |  | RB, DB&B, RF |  |  |  | f)
[5 empty] | 0.5 |  | 4 |  | CBAD11R |  |  | FB, DB&B, RF |  |  |  | f)
NOTES: | a) | Deleted
| b) | Flanged fabricated spools in nominal size 3" and above, shall be hot
dip galvanized in accordance with EDS NGZ1
| c) | ASME B16.5 NPT threaded flanges shall only be used complete with safety bleed plug as
described in Piping Detail Standard, BD01-AK-P-06016.
| d) | "SCR-connections" shall only be used during repair of existing scr-systems.
| e) | Deleted
| f) | Maximum operating temperature 30°C
| g) | Ref. TCD 4583, section 2.2.7.8
| h) | Pipe class to be used for maintenance of existing systems only