## AP02
Title | [8 empty] | Doc.no. |  |  | Operator |  |  | Sec.no.
Piping and Valve Specification | [8 empty] | 5060 | [5 empty] | 3
[9 empty] | Project | [5 empty] | Rev.no. |  | Rev.date |  | Page: Of:
Piping Class Sheet: |  |  | AP02 |  | b) |  | CL150 | [7 empty] | 02 |  | 01.10.2010 |  | 1 | 2
DESIGN CODE: |  |  | ASME B31.3 | [5 empty] | Corr. Allow: | [5 empty] | Material Selection : TCD 4650
Maximum Design Pressure: |  |  |  |  | Barg |  | 16 | 16 | 16 | 11.6
At Temperature: |  |  |  |  | °C |  | -15 | 38 | 66 | 93
LINER THICKNESS: |  |  |  | No Internal, External 0.3 mm | [6 empty] | f)
PIPE SIZE AND WALL THICKNESS
Nom.Size(in) |  |  |  |  | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 24
Ins. Dia.(mm) |  |  |  |  | 53.2 | 81.8 | 105.2 | 159 | 208.8 | 262.9 | 313.7 | 344.4 | 393.7 | 433.8 | 482.1 | 578.6
Wall th.(mm) |  |  |  |  | 3.1 | 3.1 | 4.1 | 3 | 3 | 3.1 | 3.8 | 4.2 | 4.8 | 5.3 | 5.9 | 7
c)
WALL THICKNESS UNDER TOLERANCES: |  |  |  |  | 8: 0; 10: %
LONGITUDINAL WELD EFFICIENCY: |  |  |  |  | 8: N/A
ELEMENT |  | DIMENSION STANDARDS |  |  | 8: NOM. SIZE; 12: TYPE; 20: MATERIAL |  | MDS | EDS
NAME |  |  |  |  | 8: FROM TO; 20: NAME
[9 empty] | incl | incl
PIPE |  | ISO 14692, Part 3 |  |  | 6: b); 8: 2; 10: 24; 20: GRE
FITTINGS |  | ISO 14692, Part 3 |  |  | 6: b); 8: 2; 10: 24; 20: GRE
BRANCHES |  | ISO 14692, Part 3 |  |  | 6: b); 8: 2; 10: 24; 20: GRE
BONDED |  | ISO 14692, Part 3 |  |  | 6: b); 8: 2; 10: 24; 12: Quick-lock; 20: GRE
JOINT |  |  |  |  | 12: Taper taper
FLANGES |  | ISO 14692, Part 3 |  |  | 6: b),d); 8: 2; 10: 24; 12: Female ends CL150; 20: GRE
FF Heavy duty
FLG. BLIND |  | ISO 14692, Part 3 |  |  | 6: b); 8: 2; 10: 24; 20: GRE
LINE BLINDS |  | Spect. blind |  |  | 8: 2; 10: 12; 12: CL150 FF; 20: B265 Gr.2 |  | T01 | NLB1
|  | Spade/spacer |  |  | 8: 14; 10: 24; 12: CL150 FF; 20: B265 Gr.2 |  | T01 | NLB1
BOLTING | i) | ASME B16.5 |  |  | 6: g); 12: Stud bolts galv.; 20: A320 L7 |  | C100
[5 empty] | 6: g); 12: Hex. nuts galv.; 20: A194 7 |  | C100
[5 empty] | 12: Stud bolts; 20: A276 S32750/760 |  | D57X | NBO1
[5 empty] | 12: Hex. Nuts; 20: A276 S32750/760 |  | D57X | NBO1
WASHER |  | ASME B18.22 |  |  | 12: Round galv.; 20: C.S.
to ASTM A153
GASKET |  |  |  |  | 8: 2; 10: 24; 12: G-ST P/S Profile Chloroprene, 63°±5° Shore A |  |  | EGA2
SAFETY |  |  |  |  | 6: e); 8: 0.5; 10: 0.75; 12: NPT (M); 20: B381 F2 |  | T01 | EFI4
BLEED PLUG | [18 empty] | EPI1
NOTES: | See page 2
Title |  |  |  |  | 8: Doc.no.; 14: Operator; 20: Sec.no.
Piping and Valve Specification |  |  |  |  | 8: 5060; 20: 3
[5 empty] | 8: Project; 20: Rev.no. | Rev.date |  | Page: Of:
Piping Class Sheet: |  |  | AP02 |  | 2: b); 4: CL150; 20: 02 | 01.10.2010 |  | 2 | 2
VALVE OR |  | VSM |  |  | 2: NOMINAL SIZE; 8: VDS; 14: REMARKS
EQUIPMENT |  |  |  |  | 2: FROM; 4: TO
TYPE |  |  |  |  | 2: incl; 4: incl
GATE |  |  |  |  | 2: 2; 4: 24; 8: GTAD11R; 14: RF | h)
BUTTERFLY |  |  |  |  | 2: 3; 4: 24; 8: BUAD21R; 14: Wafer, RF | h)
GLOBE |  |  |  |  | 2: 2; 4: 24; 8: GBAD11R; 14: RF | h)
CHECK |  |  |  |  | 2: 2; 4: 24; 8: CHAD51R; 14: Wafer, dual disc, RF | h)
BALL |  |  |  |  | 2: 2; 4: 10; 8: BLAD01R; 14: RB, RF | h)
[5 empty] | 2: 2; 4: 8; 8: BLAD11R; 14: FB, RF | h)
NOTES: | a) | Deleted
| b) | Wall thickness is based on ISO 14692 using the following safety factors and design stress
LTHS 151.3 N/mm²
|  | F1 = 0,89 |  |  | 8: A1 = 1 <=65ºC; 20: A1 = 0.727 @ 93º C
|  | F2 = 0,89 |  |  | 8: A2 = 1
|  | F3 = 0,74 |  |  | 8: A3 = 1
F3 is based on 5 N/mm² bending stress
For diameter > 4" a minimum wall thickness of 3 mm is dictated
| c) | For diameters 2" and up it is advisedable to perform a stress analysis to confirm the suitability of the
wall thickness used
| d) | Heavy duty flanges suitable for use against ASME B16.5 raised face flanges & wafer type valves
| e) | ASME B16.5 NPT threaded flanges shall only be used complete with safety bleed plug as
described in Piping Detail Standard, BD01-AK-P-06016.
| f) | Fluid composition or intended service to dictate necessity of liner. To be advised by supplier
| g) | To be supplied by selected supplier
| h) | Max. allowable operating temperature 20°C (limited to liquids containing oxygene and seawater services)
| i) | 25Cr duplex bolting to be used on continuous flow seawater cooling supply lines, or on other normally
cold lines where water can condense. 25Cr duplex bolting shall be considered for flanges without access
for inspection (e.g. fire insulated flanges).
All bolt material selection, with or without coating, shall be approved by COPSAS TA material engineer.