## AT01
Title | [8 empty] | Doc.no. |  |  | Operator |  |  | Sec.no.
Piping and Valve Specification | [8 empty] | 5060 | [5 empty] | 3
[9 empty] | Project | [5 empty] | Rev.no. |  | Rev.date |  |  | Page: Of:
Piping Class Sheet: |  |  | AT01 |  |  |  | CL150 | [7 empty] | 05 |  | 01.10.2010 |  |  | 1 | 2
DESIGN CODE: |  |  | ASME B31.3 | [5 empty] | Corr. Allow: |  |  | 0.0 | mm |  | Material Selection : TCD 4650
Maximum Design Pressure: |  |  |  |  | Barg |  | 19.6 | 19.6 | 19.2 | 15.0
At Temperature: |  |  |  |  | °C |  | -29 | 38 | 50 | 100 | f)
PIPE SIZE AND WALL THICKNESS
Nom.Size(in) | 0.5 | 0.75 | 1 | 1.5 | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 24 | 30 | 36
Dia.(mm) | 21.3 | 26.7 | 33.4 | 48.3 | 60.3 | 88.9 | 114.3 | 168.3 | 219.1 | 273.1 | 323.9 | 355.6 | 406.4 | 457.2 | 508.0 | 609.6 | 762.0 | 914.0
Wall th.(mm) | 2.77 | 2.87 | 3.38 | 3.68 | 2.77 | 3.05 | 3.05 | 3.4 | 3.76 | 4.19 | 4.57 | 4.78 | 4.78 | 4.78 | 5.54 | 6.35 | 7.92 | 9.53
Schedule |  | 40S | [8 empty] | 10S | [6 empty] | STD
Nom.Size(in) | 0.5 | 0.75 | 1 | 1.5 | 2
Dia.(mm) | 21.3 | 26.7 | 33.4 | 48.3 | 60.3
Wall th.(mm) | 3.73 | 3.91 | 4.55 | 5.08 | 5.54
Schedule |  | 80S |  | i)
WALL THICKNESS UNDER TOLERANCES: | [8 empty] | -12.5 | % | c)
LONGITUDINAL WELD EFFICIENCY: | [8 empty] | 0.80 < 16" 1.0 > 16"
ELEMENT |  | DIMENSION STANDARDS | [6 empty] | NOM. SIZE |  | TYPE |  |  |  | MATERIAL |  |  |  | MDS | EDS
NAME | [8 empty] | FROM TO | [5 empty] | NAME
[9 empty] | incl | incl
PIPE |  | ASME B36.19M | [6 empty] | 0.5 | 8 | Seamless; PE |  |  |  | B861 Gr. 2 |  |  |  | T01
|  | ASME B36.19M | [5 empty] | i) | 0.5 | 2 | Seamless; TE, NPT |  |  |  | B861 Gr. 2 |  |  |  | T01 | EPI1
|  | ASME B36.19M | [6 empty] | 0.5 | 14 | Welded, >8" BE |  |  |  | B862 Gr. 2 |  |  |  | T01
|  | ASME B36.19M/10M | [6 empty] | 16 | 36 | Welded, BE |  |  |  | B862 Gr. 2 S1.2.1 |  |  |  | T01
BENDING |  | Made from pipe | [17 empty] | NBE1
FITTINGS |  | ASME B16.11 | [5 empty] | i) | 0.5 | 2 | Coupling CL3000 THR |  |  |  | B363 WPT2 |  |  |  | T01 | EPI1
NPT
|  | ASME B16.9 | [6 empty] | 0.5 | 8 |  |  |  |  | B363 WPT2 |  |  |  | T01 | EFI1
|  | ASME B16.9 | [6 empty] | 0.5 | 14 |  |  |  |  | B363 WPT2W |  |  |  | T01 | EFI1
|  | ASME B16.9 | [6 empty] | 16 | 36 |  |  |  |  | B363 WPT2W S2.1 |  |  |  | T01 | EFI1
BRANCHES |  | Olets, lightweight | [12 empty] | B381 F2 |  |  |  | T01 | EBR2/
NOL1
|  | ASME B16.9 | [6 empty] | As fittings | [5 empty] | B363 WPT2 |  |  |  | T01 | EBR2
[15 empty] | B363 WPT2W |  |  |  | T01 | EBR2
[15 empty] | B363 WPT2W S2.1 |  |  |  | T01 | EBR2
REINFORCED |  | Drilled to | [6 empty] | 1 | 2 | CL150 RF WN |  |  |  | B381 F2 |  |  |  | T01 | EBR2/
NIPOFLANGE |  | ASME B16.5 | [17 empty] | NOL1
LAP JOINT |  | ASME B16.9 | [6 empty] | 6 | 24 | Short pattern |  |  |  | A363 Gr.2 |  |  |  | T01
STUB END
LAP JOINT |  | ASME B16.9 | [5 empty] | j) | 1.5 | 8 | Made from pipe |  |  |  | B861 Gr.2 |  |  |  | T01 | NBE1
FLARED END
LAP JOINT |  | ASME B16.5 | [6 empty] | 6 | 24 |  |  |  |  | A182 F316 |  |  |  | S01
FLANGE | [7 empty] | j) | 1.5 | 4 |  |  |  |  | A182 F316 |  |  |  | S01
[8 empty] | d) | 6 | 24 |  |  |  |  | B381 F2 |  |  |  | T01
FLANGES |  | ASME B16.5 | [6 empty] | 0.5 | 24 | CL150 RF WN |  |  |  | B381 F2 |  |  |  | T01 | NAF1
|  | ASME B16.47 Series A | [6 empty] | 30 | 36 | CL150 RF WN |  |  |  | B381 F2 |  |  |  | T01 | NAF1
FLG. BLIND |  | ASME B16.5 | [6 empty] | 0.5 | 24 | CL150 RF |  |  |  | B381 F2 |  |  |  | T01 | NAF1
|  | ASME B16.47 Series A | [6 empty] | 30 | 36 | CL150 RF |  |  |  | B381 F2 |  |  |  | T01 | NAF1
ORIF.FLANGES |  | ASME B16.36 | [6 empty] | 1 | 24 | CL300 RF WN |  |  |  | B381 F2 |  |  |  | T01 | NAF1
RED. THR'D |  | ASME B16.5 | [5 empty] | g) | 0.75 | 2 | CL150 RF NPT (F) |  |  |  | B381 F2 |  |  |  | T01 | NAF1/
FLANGE | [19 empty] | EPI1
LINE BLINDS |  | Spect bl. | [6 empty] | 0.5 | 12 | CL150 FF |  |  |  | B381 F2 |  |  |  | T01 | NLB1
[9 empty] | 0.5 | 12 | CL150 FF |  |  |  | B265 Gr.2 |  |  |  | T01 | NLB1
|  | Spade/spacer | [6 empty] | 14 | 36 | CL150 FF |  |  |  | B381 F2 |  |  |  | T01 | NLB1
[9 empty] | 14 | 36 | CL150 FF |  |  |  | B265 Gr.2 |  |  |  | T01 | NLB1
BOLTING | h) | ASME B16.5/B16.47 Series A | [6 empty] | 0.5 | 36 | Stud bolts galv. |  |  |  | A320 L7 |  |  |  | C100 | NBO1
[9 empty] | 0.5 | 36 | Hex. nuts galv. |  |  |  | A194 7 |  |  |  | C100 | NBO1
[9 empty] | 0.5 | 36 | Stud bolts |  |  |  | A276 S32750/760 |  |  |  | D57X | NBO1
[9 empty] | 0.5 | 36 | Hex. Nuts |  |  |  | A276 S32750/760 |  |  |  | D57X | NBO1
[8 empty] | d) | 0.5 | 36 | Stud bolts |  |  |  | F468 grade 5 or 19 |  |  |  | T03 | NBO1
[8 empty] | d) | 0.5 | 36 | Hex. nuts |  |  |  | F467 grade 5 or 19 |  |  |  | T03 | NBO1
GASKET |  | ASME B16.20 | [5 empty] | e) | 0.5 | 2 | 4.5 mm thk. SPW titanium rings w/PTFE filler | [8 empty] | EGA6
|  | ASME B16.21 | [6 empty] | 0.5 | 36 | Thickness 1.5 mm Gl.fibre w/NBR.binder | [8 empty] | NGA2
PLUGS |  | ASME B16.11 | [6 empty] | 0.5 | 1 | Hex. head |  |  |  | B381 F2 |  |  |  | T01 | EPI1
SAFETY | [7 empty] | g) | 0.5 | 0.75 | NPT (M) |  |  |  | B381 F2 |  |  |  | T01 | EFI4/
BLEED PLUG | [19 empty] | EPI1
NOTES: | See page 2.
Title | [8 empty] | Doc.no. |  |  | Operator |  |  | Sec.no.
Piping and Valve Specification | [8 empty] | 5060 | [5 empty] | 3
[9 empty] | Project | [5 empty] | Rev.no. |  | Rev.date |  |  | Page: Of:
Piping Class Sheet: |  |  | AT01 |  |  |  | CL150 | [7 empty] | 05 |  | 01.10.2010 |  |  | 2 | 2
VALVE OR |  | VSM |  |  | NOMINAL SIZE |  |  |  | VDS |  |  | REMARKS
EQUIPMENT |  |  |  |  | FROM |  | TO
TYPE |  |  |  |  | incl |  | incl
GATE |  |  |  |  | 0.5 |  | 3 |  | GTAT00R |  |  | RF
[5 empty] | 2 |  | 36 |  | GTAT10R |  |  | RF
BUTTERFLY |  |  |  |  | 3 |  | 36 |  | BUAT20R |  |  | Wafer, RF
[5 empty] | 3 |  | 36 |  | BUAT30R |  |  | Wafer, Metal seated, RF
GLOBE |  |  |  |  | 0.5 |  | 1.5 |  | GBBT00B |  |  | BW
[5 empty] | 2 |  | 24 |  | GBAT10R |  |  | RF
CHECK |  |  |  |  | 0.5 |  | 1.5 |  | CHBT01B |  |  | BW
[5 empty] | 0.5 |  | 2 |  | CHAT00R |  |  | RF
[5 empty] | 2 |  | 36 |  | CHAT50R |  |  | Wafer, RF
[5 empty] | 2 |  | 36 |  | CHAT90R |  |  | Non-slam, RF
BALL |  |  |  |  | 0.5 |  | 10 |  | BLAT00R |  |  | RB, RF
[5 empty] | 0.5 |  | 8 |  | BLAT10R |  |  | FB, RF
[5 empty] | 2 |  | 36 |  | BLAT30R |  |  | RB, RF
[5 empty] | 2 |  | 36 |  | BLAT40R |  |  | FB, RF
[5 empty] | 4 |  | 36 |  | BLAT50R |  |  | RB, Metal seated, RF
[5 empty] | 4 |  | 36 |  | BLAT60R |  |  | FB, Metal seated, RF
MODULAR |  |  |  |  | 0.5 |  | 2 |  | CBAT20D |  |  | SB, DB&B, RF/TE
[5 empty] | 0.5 |  | 4 |  | CBAT00R |  |  | RB, DB&B, RF
[5 empty] | 0.5 |  | 4 |  | CBAT10R |  |  | FB, DB&B, RF
[5 empty] | 0.5 |  | 2 |  | CBAT70D |  |  | SB, Metal seat, DB&B, RF/TE
[5 empty] | 0.5 |  | 2 |  | CBAT90D |  |  | SB, DB&B, RF/TE
NOTES: | a) | Deleted
| b) | This piping class is suitable for sour service according to ISO 15156/NACE MR-01-075
| c) | The tolerance is used for design and is not part of the purchase specification
when deviating from the individual piping item.
| d) | Use for submerged/seawater exposed lines only.
| e) | Use for Sodium Hypochlorite only. AT01 revision 04 and earlier specified 1.5mm reinforced PTFE gasket.
| f) | Max. allowable operating temperature 90°C
| g) | ASME B16.5 NPT threaded flanges shall only be used complete with safety bleed plug as
described in Piping Detail Standard, BD01-AK-P-06016.
| h) | 25Cr duplex bolting to be used on continuous flow seawater cooling supply lines, or on other normally
cold lines where water can condense. 25Cr duplex bolting shall be considered for flanges without access
for inspection (e.g. fire insulated flanges).
All bolt material selection, with or without coating, shall be approved by COPSAS TA material engineer.
| i) | NPT connections only to be used for normally dry deluge systems, piping wall thickness to be according sch. 80S
| j) | Use for Fire Water system only