## AV12
Title | [8 empty] | Doc.no. |  |  | Operator |  |  | Sec.no.
Piping and Valve Specification | [8 empty] | 5060 | [5 empty] | 3
[9 empty] | Project | [5 empty] | Rev.no. |  | Rev.date |  |  | Page: Of:
Piping Class Sheet: |  |  | AV12 |  | e) f) |  | CL150 | [7 empty] | 05 |  | 01.10.2010 |  |  | 1 | 2
DESIGN CODE: |  |  | ASME B31.3 | [5 empty] | Corr. Allow: |  |  | 5.0 | mm |  | Material Selection : TCD 4650
Maximum Design Pressure: |  |  |  |  | Barg |  | 20.0 | 20.0 | 19.2 | 17.7 | 15.8 | 14.0 | 12.1 | 10.2
At Temperature: |  |  |  |  | °C |  | -101 | 38 | 50 | 100 | 150 | 200 | 250 | 300
PIPE SIZE AND WALL THICKNESS
Nom.Size(in) | 0.5 | 0.75 | 1 | 1.5 | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 24 | 30 | 36
Dia.(mm) | 21.3 | 26.7 | 33.4 | 48.3 | 60.3 | 88.9 | 114.3 | 168.3 | 219.1 | 273.1 | 323.9 | 355.6 | 406.4 | 457.2 | 508.0 | 609.6 | 762.0 | 914.0
Wall th.(mm) | 7.47 | 7.82 | 9.09 | 7.14 | 8.74 | 7.62 | 8.56 | 7.11 | 8.18 | 7.80 | 8.38 | 9.53 | 9.53 | 9.53 | 12.7 | 12.7 | 12.7 | 12.7
Schedule |  | XXS |  | 160 |  | 80 |  | 40 |  | 30 |  |  | STD |  |  | XS
WALL THICKNESS UNDER TOLERANCES: | [8 empty] | -12.5 | % | c)
LONGITUDINAL WELD EFFICIENCY: | [8 empty] | 1.0
ELEMENT |  | DIMENSION STANDARDS | [6 empty] | NOM. SIZE |  | TYPE |  |  |  | MATERIAL |  |  |  | MDS | EDS
NAME | [8 empty] | FROM TO | [5 empty] | NAME
[9 empty] | incl | incl
PIPE |  | ASME B36.10M | [6 empty] | 0.5 | 24 | Seamless, BE |  |  |  | A333 Gr.3 |  |  |  | V31
[9 empty] | 30 | 36 | Welded, BE |  |  |  | A671 Gr. CF71 |  |  |  | V32
BENDING |  | Made from pipe | [17 empty] | NBE1
FITTINGS |  | ASME B16.9 | [6 empty] | 0.5 | 36 |  |  |  |  | A420 Gr. WPL3 |  |  |  | V32 | EFI1
BRANCHES |  | Olets | [12 empty] | A350 LF3 |  |  |  | V33 | EBR3/
NOL1
|  | ASME B16.9 | [6 empty] | As fittings | [5 empty] | A420 Gr. WPL3 |  |  |  | V32 | EBR3
PIPE NIPPLE |  | ASTM A733 | [6 empty] | 0.5 | 1 | Sch XXS BOE/TOE |  |  |  | A333 Gr.3 |  |  |  | V31 | EPI1
REINFORCED |  | Drilled to | [6 empty] | 1 | 2 | CL150 RF WN |  |  |  | A350 LF3 |  |  |  | V33 | EBR3/
NIPOFLANGE |  | ASME B16.5 | [17 empty] | NOL1
FLANGES |  | ASME B16.5 | [6 empty] | 0.5 | 24 | CL150 RF WN |  |  |  | A350 LF3 |  |  |  | V33 | NAF1
|  | ASME B16.47 Series A | [6 empty] | 30 | 36 | CL150 RF WN | [8 empty] | NAF1
FLG. BLIND |  | ASME B16.5 | [6 empty] | 0.5 | 24 | CL150 RF |  |  |  | A350 LF3 |  |  |  | V33 | NAF1
|  | ASME B16.47 Series A | [6 empty] | 30 | 36 | CL150 RF | [8 empty] | NAF1
ORIF.FLANGES |  | ASME B16.36 | [6 empty] | 1 | 24 | CL300 RF WN |  |  |  | A350 LF3 |  |  |  | V33 | NAF1
RED. THR'D |  | ASME B16.5 |  |  |  |  | d) |  | 0.75 | 2 | CL150 RF NPT (F) |  |  |  | A350 LF3 |  |  |  | V33 | NAF1
FLANGE | [19 empty] | EPI1
LINE BLINDS |  | Spect bl. | [6 empty] | 0.5 | 12 | CL150 FF |  |  |  | A350 LF3 |  |  |  | V33 | NLB1
[9 empty] | 0.5 | 12 | CL150 FF |  |  |  | A203 Gr. E |  |  |  | V33 | NLB1
|  | Spade/spacer | [6 empty] | 0.5 | 12 | CL150 FF |  |  |  | A350 LF3 |  |  |  | V33 | NLB1
[9 empty] | 14 | 36 | CL150 FF |  |  |  | A203 Gr. E |  |  |  | V33 | NLB1
BOLTING |  | ASME B16.5 | [8 empty] | Stud bolts galv. |  |  |  | A320 L7 |  |  |  | C100 | NBO1
[11 empty] | Hex. nuts galv. |  |  |  | A194 7 |  |  |  | C100 | NBO1
GASKET |  | ASME B16.20 | [8 empty] | 4.5 mm thk. SPW 316L w/Exp. | [8 empty] | EGA1
Graphite int/ext. ring 316L SS
PLUGS |  | ASME B16.11 | [6 empty] | 0.5 | 1 | Hex. head |  |  |  | A350 LF3 |  |  |  | V33 | EPI1
SAFETY | [6 empty] | d) |  | 0.5 | 0.75 | NPT (M) |  |  |  | B446 N06625 |  |  |  |  | EFI4/
BLEED PLUG | [14 empty] | Annealed |  |  |  |  | EPI1
NOTES: | See page 2
Title | [8 empty] | Doc.no. |  |  | Operator |  |  | Sec.no.
Piping and Valve Specification | [8 empty] | 5060 | [5 empty] | 3
[9 empty] | Project | [5 empty] | Rev.no. |  | Rev.date |  |  | Page: Of:
Piping Class Sheet: |  |  | AV12 |  | e) f) |  | CL150 | [7 empty] | 05 |  | 01.10.2010 |  |  | 2 | 2
VALVE OR |  | VSM |  |  | NOMINAL SIZE |  |  |  | VDS |  |  | REMARKS
EQUIPMENT |  |  |  |  | FROM |  | TO
TYPE |  |  |  |  | incl |  | incl
GATE |  |  |  |  | 0.5 |  | 2 |  | GTAV00R |  |  | RF
[5 empty] | 2 |  | 36 |  | GTAV10R |  |  | RF
[5 empty] | 2 |  | 36 |  | GTAV30R |  |  | RB, Through conduit slab, Max. 200°C, RF
[5 empty] | 2 |  | 36 |  | GTAV40R |  |  | FB, Through conduit slab, Max. 200°C, RF
[5 empty] | 2 |  | 36 |  | GTAV70R |  |  | Through conduit, Double expanding, Max. 200°C, RF
BUTTERFLY |  |  |  |  | 3 |  | 36 |  | BUAV30R |  |  | Wafer, Metal seated, Max. 200°C, RF
GLOBE |  |  |  |  | 0.5 |  | 2 |  | GBAV00R |  |  | RF
[5 empty] | 2 |  | 24 |  | GBAV10R |  |  | RF
CHECK |  |  |  |  | 0.5 |  | 2 |  | CHAV00R |  |  | RF
[5 empty] | 2 |  | 4 |  | CHAV20R |  |  | Swing, RF
[5 empty] | 2 |  | 36 |  | CHAV50R |  |  | Wafer, Dual disc, RF
[5 empty] | 2 |  | 36 |  | CHAV90R |  |  | Non-slam, RF
BALL |  |  |  |  | 0.5 |  | 10 |  | BLAV00R |  |  | RB, Max 150°C, RF
[5 empty] | 0.5 |  | 8 |  | BLAV10R |  |  | FB, Max 150°C, RF
[5 empty] | 2 |  | 36 |  | BLAV30R |  |  | RB, Max 150°C, RF
[5 empty] | 2 |  | 36 |  | BLAV40R |  |  | FB, Max 150°C, RF
[5 empty] | 4 |  | 36 |  | BLAV50R |  |  | RB, Metal seat, Max. 200°C, RF
[5 empty] | 4 |  | 36 |  | BLAV60R |  |  | FB, Metal seat, Max. 200°C, RF
MODULAR |  |  |  |  | 0.5 |  | 2 |  | CBAV20D |  |  | SB, DB&B, Max. 150°C, RF/TE
[5 empty] | 0.5 |  | 4 |  | CBAV00R |  |  | RB, DB&B, Max. 150°C, RF
[5 empty] | 0.5 |  | 4 |  | CBAV10R |  |  | FB, DB&B, Max. 150°C, RF
[5 empty] | 0.5 |  | 2 |  | CBAV70D |  |  | SB, Metal seat, DB&B, RF/TE
[5 empty] | 0.5 |  | 2 |  | CBAV90D |  |  | SB, DB&B, Max. 150°C, RF/TE
NOTES: | a) | Deleted
| b) | Deleted
| c) | The tolerance is used for design and is not part of the purchase specification
when deviating from the individual piping item.
| d) | ASME B16.5 NPT threaded flanges shall only be used complete with safety bleed plug as
described in Piping Detail Standard, BD01-AK-P-06016.
| e) | Deleted
| f) | Pipe class to be used for maintenance of existing systems only