## FV10
Title | [8 empty] | Doc.no. |  |  | Operator |  |  | Sec.no.
Piping and Valve Specification | [8 empty] | 5060 | [5 empty] | 3
[9 empty] | Project | [5 empty] | Rev.no. |  | Rev.date |  | Page: Of:
Piping Class Sheet: |  |  | FV10 |  | e) |  | CL1500 | [7 empty] | 05 |  | 01.10.2010 |  | 1 | 2
DESIGN CODE: |  |  | ASME B31.3 | [5 empty] | Corr. Allow: |  |  | 1.5 | mm |  | Material Selection : TCD 4650
Maximum Design Pressure: |  |  |  |  | Barg |  | 258.6 | 258.6 | 258.6 | 238.0 | 230.8
At Temperature: |  |  |  |  | °C |  | -101 | 38 | 50 | 100 | 150
PIPE SIZE AND WALL THICKNESS
Nom.Size(in) | 0.5 | 0.75 | 1 | 1.5 | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 24
Dia.(mm) | 21.3 | 26.7 | 33.4 | 48.3 | 60.3 | 88.9 | 114.3 | 168.3 | 219.1 | 273.1 | 323.9 | 355.6 | 406.4 | 457.2 | 508.0 | 609.6
Wall th.(mm) | 4.78 | 5.56 | 6.35 | 7.14 | 8.74 | 11.13 | 13.49 | 18.26 | 23.01 | 28.58 | 33.32 | 35.71 | 40.49 | 45.24 | 50.01 | 59.54
Schedule | [8 empty] | 160
WALL THICKNESS UNDER TOLERANCES: | [9 empty] | -12.5 | % | c)
LONGITUDINAL WELD EFFICIENCY: | [9 empty] | 1.0
ELEMENT |  | DIMENSION STANDARDS | [6 empty] | NOM. SIZE |  | TYPE |  |  |  | MATERIAL |  |  | MDS | EDS
NAME | [8 empty] | FROM TO | [5 empty] | NAME
[9 empty] | incl | incl
PIPE |  | ASME B36.10M | [6 empty] | 0.5 | 24 | Seamless, BE |  |  |  | A333 Gr.3 |  |  | V31
[9 empty] | 2 | 24 | Welded, BE |  |  |  | A671 Gr. CF71 |  |  | V32
BENDING |  | Made from pipe | [16 empty] | NBE1
FITTINGS |  | ASME B16.9 | [6 empty] | 0.5 | 24 |  |  |  |  | A420 Gr. WPL3 |  |  | V32 | EFI1
BRANCHES |  | Olets | [12 empty] | A350 LF3 |  |  | V33 | EBR3/
NOL1
|  | ASME B16.9 | [6 empty] | As fittings | [5 empty] | A420 Gr. WPL3 |  |  | V32 | EBR3
PIPE NIPPLE |  | ASTM A733 | [6 empty] | 0.5 | 1.5 | Sch XXS BOE/TOE |  |  |  | A333 Gr.3 |  |  | V31 | EPI1
Bev to match sch 160
REINFORCED |  | Drilled to | [6 empty] | 1 | 2 | CL1500 RTJ WN |  |  |  | A350 LF3 |  |  | V33 | EBR3/
NIPOFLANGE |  | ASME B16.5 | [16 empty] | NOL1
FLANGES |  | ASME B16.5 | [6 empty] | 0.5 | 24 | CL1500 RTJ WN |  |  |  | A350 LF3 |  |  | V33 | NAF1
FLG. BLIND |  | ASME B16.5 | [6 empty] | 0.5 | 24 | CL1500 RTJ WN |  |  |  | A350 LF3 |  |  | V33 | NAF1
ORIF.FLANGES |  | ASME B16.36 | [6 empty] | 0.5 | 24 | CL1500 RTJ WN |  |  |  | A350 LF3 |  |  | V33 | NAF1
RED. THR'D |  | ASME B16.5 | [5 empty] | d) | 0.75 | 2 | CL1500 RTJ NPT (F) |  |  |  | A350 LF3 |  |  | V33 | NAF1/
FLANGE | [18 empty] | EPI1
LINE BLINDS |  | Spect bl. | [6 empty] | 0.5 | 6 | CL1500 RTJ |  |  |  | A350 LF3 |  |  | V33 | NLB1
[9 empty] | 0.5 | 6 | CL1500 RTJ |  |  |  | A203 Gr. E |  |  | V33 | NLB1
|  | Spade/ spacer | [6 empty] | 0.5 | 6 | CL1500 RTJ |  |  |  | A350 LF3 |  |  | V33 | NLB1
[9 empty] | 8 | 24 | CL1500 RTJ |  |  |  | A203 Gr. E |  |  | V33 | NLB1
BOLTING |  | ASME B16.5 | [6 empty] | 0.5 | 16 | Stud bolts galv. |  |  |  | A320 L7 |  |  | C100 | NBO1
[9 empty] | 18 | 24 | Stud bolts galv. |  |  |  | A320 L43 |  |  | C100 | NBO1
[9 empty] | 0.5 | 24 | Hex. nuts galv. |  |  |  | A194 7 |  |  | C100 | NBO1
GASKET |  | ASME B16.20 | [5 empty] | f) | 0.5 | 24 | Octagonal ring |  |  |  | AISI 316 |  |  |  | NGA3
PLUGS |  | ASME B16.11 | [6 empty] | 0.5 | 1 | Hex. head |  |  |  | A350 LF3 |  |  | V33 | EPI1
SAFETY | [7 empty] | d) | 0.5 | 0.75 | NPT (M) |  |  |  | B446 N06625 |  |  |  | EFI4/
BLEED PLUG | [14 empty] | Annealed |  |  |  | EPI1
NOTES: | See page 2
Title | [8 empty] | Doc.no. |  |  | Operator |  |  | Sec.no.
Piping and Valve Specification | [8 empty] | 5060 | [5 empty] | 3
[9 empty] | Project | [5 empty] | Rev.no. |  | Rev.date |  | Page: Of:
Piping Class Sheet: |  |  | FV10 |  | e) |  | CL1500 | [7 empty] | 05 |  | 01.10.2010 |  | 2 | 2
VALVE OR |  | VSM |  |  | NOMINAL SIZE |  |  |  | VDS |  |  | REMARKS
EQUIPMENT |  |  |  |  | FROM |  | TO
TYPE |  |  |  |  | incl |  | incl
GATE |  |  |  |  | 0.5 |  | 1 |  | GTFV01B |  |  | BW
[5 empty] | 0.5 |  | 2 |  | GTFV01J |  |  | RTJ
[5 empty] | 2 |  | 24 |  | GTFV11J |  |  | RTJ
GLOBE |  |  |  |  | 0.5 |  | 1 |  | GBFV01B |  |  | BW
[5 empty] | 0.5 |  | 2 |  | GBFV01J |  |  | RTJ
[5 empty] | 2 |  | 24 |  | GBFV11J |  |  | RTJ
CHECK |  |  |  |  | 0.5 |  | 1 |  | CHFV01B |  |  | BW
[5 empty] | 0.5 |  | 2 |  | CHFV01J |  |  | RTJ
[5 empty] | 2 |  | 24 |  | CHFV51J |  |  | Wafer, Dual disc, RTJ
BALL |  |  |  |  | 2 |  | 24 |  | BLFV50J |  |  | RB, Metal seated, RTJ
[5 empty] | 2 |  | 24 |  | BLFV60J |  |  | FB, Metal seated, RTJ
MODULAR |  |  |  |  | 0.5 |  | 2 |  | CBFV20D |  |  | SB, DB&B, RTJ/TE
[5 empty] | 0.5 |  | 2 |  | CBFV00J |  |  | RB, DB&B, RTJ
[5 empty] | 0.5 |  | 2 |  | CBFV10J |  |  | FB, DB&B, RTJ
[5 empty] | 2 |  | 4 |  | CBFV30J |  |  | RB, DB&B, RTJ
[5 empty] | 2 |  | 4 |  | CBFV40J |  |  | FB, DB&B, RTJ
[5 empty] | 0.5 |  | 2 |  | CBFV70D |  |  | SB, Metal seat, DB&B, RTJ/TE
[5 empty] | 0.5 |  | 2 |  | CBFV90D |  |  | SB, DB&B, RTJ/TE
| a) | Deleted
| b) | Deleted
| c) | The tolerance is used for design and is not part of the purchase specification
when deviating from the individual piping item.
| d) | ASME B16.5 NPT threaded flanges shall only be used complete with safety bleed plug as
described in Piping Detail Standard, BD01-AK-P-06016.
| e) | Deleted
| f) | Oval ring for NPS 0.5" - 16" has been specified previous to FV10 revision 02 dated 28.11.2002