## GD12
Title | [8 empty] | Doc.no. |  |  | Operator |  | Sec.no.
Piping and Valve Specification | [8 empty] | 5060 |  |  |  |  | 3
[9 empty] | Project |  |  |  |  | Rev.no. | Rev.date |  | Page: Of:
Piping Class Sheet: |  |  | GD12 |  |  |  | CL2500 | [6 empty] | 06 | 2010-10-01 |  | 1 | 2
DESIGN CODE: |  |  | ASME B31.3 | [5 empty] | Corr. Allow: |  |  | 0.0 | mm | Material Selection : TCD 4650
Maximum Design Pressure: |  |  |  |  | Barg |  | 399 | 399 | 395 | 382 | 370 | 365
At Temperature: |  |  |  |  | °C |  | -46 | 38 | 50 | 100 | 150 | 170
PIPE SIZE AND WALL THICKNESS
Nom.Size(in) | 0.5 | 0.75 | 1 | 1.5 | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16
Dia.(mm) | 21.3 | 26.7 | 33.4 | 48.3 | 60.3 | 88.9 | 114.3 | 168.3 | 219.1 | 273.1 | 323.9 | 355.6 | 406.4
Wall th.(mm) | 3.73 | 3.91 | 4.55 | 5.08 | 5.54 | 11.13 | 11.13 | 18.26 | 20.62 | 25.40 | 33.32 | 31.75 | 36.53
Schedule |  | 80S |  |  |  | 160 | 120 | 160 | 140 |  | 160 | 140
WALL THICKNESS UNDER TOLERANCES: | [8 empty] | -12.5 | % | c)
LONGITUDINAL WELD EFFICIENCY: | [8 empty] | 1.0
ELEMENT |  | DIMENSION STANDARDS | [6 empty] | NOM. SIZE |  | TYPE |  |  | MATERIAL |  | MDS | EDS
NAME | [8 empty] | FROM TO |  |  |  |  | NAME
[9 empty] | incl | incl
PIPE |  | ASME B36.19M/.10M | [6 empty] | 0.5 | 8 | Seamless; >0.75" BE |  |  | A790 S32750/760 |  | D51
|  | ASME B36.10M | [6 empty] | 3 | 16 | Welded, BE |  |  | A928 S32750/760 Cl 1 or 3 |  | D52
BENDING |  | Made from pipe | [14 empty] | NBE1
FITTINGS |  | ASME B16.9 | [6 empty] | 0.5 | 16 |  |  |  | A815 S32750/760 Cl S/WX |  | D53 | EFI1
BRANCHES |  | Olets | [11 empty] | A182 F53/F55 |  | D54 | EBR3/
NOL1
|  | ASME B16.9 | [6 empty] | As fittings |  |  |  |  | A815 S32750/760 Cl S/WX |  | D53 | EBR3
PIPE NIPPLE |  | ASTM A733 | [6 empty] | 0.5 | 1.5 | Sch160 BOE/TOE |  |  | A790 S32750/760 |  | D51 | EPI1
Bev to match sch 80S
REINFORCED |  | Drilled to | [6 empty] | 1 | 2 | CL2500 RTJ WN |  |  | A182 F53/F55 |  | D54 | EBR3/
NIPOFLANGE |  | ASME B16.5 | [14 empty] | NOL1
FLANGES |  | ASME B16.5 | [6 empty] | 0.5 | 12 | CL2500 RTJ WN |  |  | A182 F53/F55 |  | D54 | NAF1
|  | Desflex Compact flange | [5 empty] | e) | 6 | 16 | CL2500 WN type |  |  | A182 F53/55 |  | D54
FLG. BLIND |  | ASME B16.5 | [6 empty] | 0.5 | 12 | CL2500 RTJ WN |  |  | A182 F53/F55 |  | D54 | NAF1
|  | Desflex Compact flange blind | [5 empty] | e) | 6 | 16 | CL2500 WN type |  |  | A182 F53/55 |  | D54
RED. THR'D |  | ASME B16.5 | [5 empty] | d) | 0.75 | 2 | CL2500 RTJ NPT (F) |  |  | A182 F53/F55 |  | D54 | NAF1/
FLANGE | [16 empty] | EPI1
LINE BLINDS |  | Spect bl. | [6 empty] | 0.5 | 4 | CL2500 RTJ |  |  | A240 S32750/760 |  | D55 | NLB1
[9 empty] | 0.5 | 4 | CL2500 RTJ |  |  | A182 F53/F55 |  | D54 | NLB1
|  | Spade/spacer | [6 empty] | 6 | 12 | CL2500 RTJ |  |  | A240 S32750/760 |  | D55 | NLB1
[9 empty] | 6 | 12 | CL2500 RTJ |  |  | A182 F53/F55 |  | D54 | NLB1
|  | Desflex Compact flg. spade/spacer | [5 empty] | e) | 6 | 16 | CL2500 |  |  | A182 F53/55 |  | D54
BOLTING | f) | ASME B16.5 | [6 empty] | 0.5 | 10 | Stud bolts galv. |  |  | A320 L7 |  | C100 | NBO1
[9 empty] | 12 | 12 | Stud bolts galv. |  |  | A320 L43 |  | C100 | NBO1
[9 empty] | 0.5 | 12 | Hex. nuts galv. |  |  | A194 7 |  | C100 | NBO1
[9 empty] | 0.5 | 12 | Stud bolts |  |  | A276 S32750/760 |  | D57X | NBO1
[9 empty] | 0.5 | 12 | Hex. Nuts |  |  | A276 S32750/760 |  | D57X | NBO1
|  | For Desflex Compact flange | [5 empty] | e) | 6 | 16 | Stud bolts galv. |  |  | A320 L7 |  | C100 | NBO1
[9 empty] | 6 | 16 | Spher.hex. nuts galv. |  |  | A194 7 |  | C100
GASKET |  | ASME B16.20 | [5 empty] | g) | 0.5 | 12 | Octagonal ring |  |  | AISI 316 |  |  | NGA3
|  | For Desflex Compact flange | [5 empty] | e) |  |  | Seal ring, PTFE coated |  |  | A182 F53/F55 |  | D54
PLUGS |  | ASME B16.11 | [6 empty] | 0.5 | 1 | Hex. head |  |  | A182 F53/F55 |  | D54 | EPI1
SAFETY | [7 empty] | d) | 0.5 | 0.75 | NPT (M) |  |  | B446 N06625 |  |  | EFI4/
BLEED PLUG | [13 empty] | Annealed |  |  | EPI1
NOTES: |  | See page 2.
Title | [8 empty] | Doc.no. |  |  | Operator |  | Sec.no.
Piping and Valve Specification | [8 empty] | 5060 |  |  |  |  | 3
[9 empty] | Project |  |  |  |  | Rev.no. | Rev.date |  | Page: Of:
Piping Class Sheet: |  |  | GD12 |  |  |  | CL2500 | [6 empty] | 06 | 40452 |  | 2 | 2
VALVE OR |  | VSM |  |  | NOMINAL SIZE |  |  |  | VDS |  |  | REMARKS
EQUIPMENT |  |  |  |  | FROM |  | TO
TYPE |  |  |  |  | incl |  | incl
GATE |  |  |  |  | 1 |  | 12 |  | GTGD10J |  |  | RTJ
[5 empty] | 2 |  | 12 |  | GTGD30J |  |  | RB, Through conduit slab, RTJ
[5 empty] | 2 |  | 12 |  | GTGD40J |  |  | FB, Through conduit slab, RTJ
[5 empty] | 2 |  | 12 |  | GTGD70J |  |  | Through conduit, Double expanding, RTJ
GLOBE |  |  |  |  | 0.5 |  | 12 |  | GBGD10J |  |  | RTJ
CHECK |  |  |  |  | 0.5 |  | 2 |  | CHGD00J |  |  | RTJ
[5 empty] | 2 |  | 12 |  | CHGD50J |  |  | Wafer, Dual disc, RTJ
[5 empty] | 2 |  | 12 |  | CHGD90J |  |  | Non-slam, RTJ
BALL |  |  |  |  | 2 |  | 12 |  | BLGD50J |  |  | RB, Metal seated, RTJ
[5 empty] | 2 |  | 12 |  | BLGD60J |  |  | FB, Metal seated, RTJ
MODULAR |  |  |  |  | 0.5 |  | 2 |  | CBGD20D |  |  | SB, DB&B, Max. 150°C, RTJ/TE
[5 empty] | 0.5 |  | 2 |  | CBGD00J |  |  | RB, DB&B, Max. 150°C, RTJ
[5 empty] | 0.5 |  | 2 |  | CBGD10J |  |  | FB, DB&B, Max. 150°C, RTJ
[5 empty] | 1 |  | 2 |  | CBGD50J |  |  | RB, Metal seat, DB&B, RTJ
[5 empty] | 1 |  | 2 |  | CBGD60J |  |  | FB, Metal seat, DB&B, RTJ
[5 empty] | 0.5 |  | 2 |  | CBGD70D |  |  | SB, Metal seat, DB&B, RTJ/TE
[5 empty] | 0.5 |  | 2 |  | CBGD90D |  |  | SB, DB&B, Max. 150°C, RTJ/TE
NOTES: | a) | Deleted
| b) | This piping class is suitable for sour service according to ISO 15156 (NACE MR-01-075)
| c) | The tolerance is used for design and is not part of the purchase specification
when deviating from the individual piping item.
Straight pipe to A358 could be utilized with undertolerance of 0.3 mm
| d) | ASME B16.5 NPT threaded flanges shall only be used complete with safety bleed plug as
described in Piping Detail Standard BD01-AK-P-06016
| e) | Use of Desflex Compact flanges shall be accepted by COMPANY and to be used only
when modifying existing piping systems with Desflex compact flanges on EKOX and EKOJ
ASME flanges shall be used for new and for modification projects.
| f) | 25Cr duplex bolting to be used on normally cold lines where water can condense. 25Cr duplex bolting shall be
considered for flanges without access for inspection (e.g. fire insulated flanges).
All bolt material selection, with or without coating, shall be approved by COPSAS TA material engineer.
| g) | Oval ring has been specified previous to GC10 revision 02 dated 29.11.2002