## Sheet1
Title | [8 empty] | Doc.no. |  |  | Operator |  | Sec.no.
Piping and Valve Specification | [8 empty] | 5060 |  |  |  |  | 3
[9 empty] | Project |  |  |  |  | Rev.no. | Rev.date |  | Page: Of:
Piping Class Sheet: |  |  | LS22 |  | i) |  | 6000psi | [6 empty] | 04 | 01.10.2010 |  | 1 | 2
DESIGN CODE: |  |  | ASME B31.3 | [5 empty] | Corr. Allow: |  |  | 0.0 | mm | Material Selection : TCD 4650
Maximum Design Pressure: |  |  |  |  | Barg |  | 350 | 350 | 350
At Temperature: |  |  |  |  | °C |  | -29 | 38 | 80
PIPE SIZE AND WALL THICKNESS
Nom.Size(in) |  |  |  | 1.5 | 2 | 3 | 4
Dia.(mm) |  |  |  | 48.3 | 60.3 | 88.9 | 114.3
Wall th.(mm) |  |  |  | 10.15 | 11.07 | 15.24 | 17.12
Schedule |  |  |  |  | XXS
WALL THICKNESS UNDER TOLERANCES: | [8 empty] | -12.5 | % | b)
LONGITUDINAL WELD EFFICIENCY: | [8 empty] | N/A
ELEMENT |  | DIMENSION STANDARDS | [6 empty] | NOM. SIZE |  | TYPE |  |  | MATERIAL |  | MDS | EDS
NAME | [8 empty] | FROM TO |  |  |  |  | NAME
[9 empty] | incl | incl
PIPE |  | ASME B36.19 | [6 empty] | 1.5 | 4 | Smls PE |  |  | A312 TP 316 |  | S01 | c)
BENDING |  | Made from pipe | [5 empty] | e) | [8 empty] | NBE1
FITTINGS |  | ASME B16.9 | [6 empty] | 1.5 | 4 | (LR for elbows) |  |  | A403 WP-316 |  | S01 | EFI1 | f)
|  | SAE J 518C Code 62 | [6 empty] | 1.5 | 2 | Retain ring type flg. |  |  | A182 F316 |  | S01 | EFI3 | d)
|  | SAE J 518C Code 62 | [6 empty] | 1.5 | 2 | Block type |  |  | A182 F316 |  | S01 | EFI3
|  | ISO 6164 400 bar | [6 empty] | 3 | 4 | Retain ring type flg. |  |  | A182 F316 |  | S01 | EFI3 | d) g)
|  | ISO 6164 400 bar | [6 empty] | 3 | 4 | Block type |  |  | A182 F316 |  | S01 | EFI3
BRANCHES |  | SAE J 518C Code 62 | [6 empty] | As fittings |  |  |  |  | A182 F316 |  | S01 | EBR4 | d)
|  | ISO 6164 400 bar | [6 empty] | As fittings |  |  |  |  | A182 F316 |  | S01 | EBR4 | d)
FLANGES |  | SAE J 518C Code 62 | [6 empty] | 1.5 | 2 | Retain ring |  |  | A182 F316 |  | S01 | c) d)
|  | ISO 6164 400 bar | [6 empty] | 3 | 3 | Retain ring |  |  | A182 F316 |  | S01 | c) d)
|  | ISO 6164 400 bar | [6 empty] | 4 | 4 | With welding hub |  |  | A182 F316 |  | S01 | c) d)
FLG. BLIND |  | SAE J 518C Code 62 | [6 empty] | 1.5 | 2 |  |  |  | A182 F316 |  | S01
|  | ISO 6164 400 bar | [6 empty] | 3 | 4 |  |  |  | A182 F316 |  | S01
BOLTING |  | UNC Threaded | [8 empty] | Socket head cap |  |  | A320 B8M, class 2 |  | S03 | NBO1
[11 empty] | screws | [5 empty] | NBO1
[11 empty] | Hex nuts |  |  | A194 8M |  | S03 | NBO1
NBO1
GASKET |  | Manufactures standard | [6 empty] | 1.5 | 4 | Bonded seal |  |  | AISI 316 + Perbunan
(Dowty type)
PLUG |  | ASME B16.11 | [6 empty] | 3/8 | 1/2 | Hex head NPT to |  |  | A276 316 |  | S01 | EPI1
ASME B1.20.1
NOTES: | See page 2
Title | [8 empty] | Doc.no. |  |  | Operator |  | Sec.no.
Piping and Valve Specification | [8 empty] | 5060 |  |  |  |  | 3
[9 empty] | Project |  |  |  |  | Rev.no. | Rev.date |  | Page: Of:
Piping Class Sheet: |  |  | LS22 |  |  |  | 6000psi | [6 empty] | 04 | 01.10.2010 |  | 2 | 2
VALVE OR |  | VSM |  |  | NOMINAL SIZE |  |  |  | VDS |  |  | REMARKS
EQUIPMENT |  |  |  |  | FROM |  | TO
TYPE |  |  |  |  | incl |  | incl
CHECK |  |  |  |  | 1.5 |  | 2 |  | CHLS02E |  |  | SAE J518C
[5 empty] | 1.5 |  | 2 |  | CHLS03E |  |  | Block type, bolted construction |  |  |  |  | h)
[5 empty] | 3 |  | 3 |  | CHLS02X |  |  | ISO 6164
BALL |  |  |  |  | 1.5 |  | 2 |  | BLLS02E |  |  | SAE J518C
[5 empty] | 1.5 |  | 2 |  | BLLS03E |  |  | Block type, bolted construction |  |  |  |  | h)
[5 empty] | 3 |  | 3 |  | BLLS02X |  |  | ISO 6164
NOTES: | a) | Deleted
| b) | The tolerance is used for design and is not part of the purchase specification
when deviating from the individual piping item.
| c) | Retain ring flange groove shall be machined on the pipe
| d) | For bonded seal (Dowty type)
| e) | Minimum radius 3D. Fabricator shall ensure that the combined effect of pipe manufacturing
tolerance and bending does not reduce the maximum design pressure when calculated
according to ASME B31.3
| f) | Buttweld fittings and connections shall be used only when connecting piping direct
to mating flanges supplied by equipment vendor.
| g) | For 4" use flanged elbow only
| h) | Drilled and tapped UNC to match SAE J 518C Code 62 flanges
| i) | Primarily for modification of existing 316SS tubing systems. For new tubing lines SDSS shall be used.